## SCOPE OF WORK
Scope of work are the lowest price for one of the below 2 options.
1. Supply, install, and commission a replacement pump. or
2. Study the intended application and operation of the pump system, to replace the VS6 pump with other possible options such as employing booster plus main pump etc. and recommend the possible option which best satisfy the indicated requirements techno-economically.
Notes from Orginal Manufacturere of old Pump
QUOTE we have checked the details that you have sent us regarding pump operation. According to the operating conditions described seems that the pump is fed by a vessel that its temperature is 100 deg.C in Atmospheric pressure. This means that the water is in boiling condition and that there is a lot of Vapor Gas- phase Dissolved within the water phase and therefore although NPSHa of the installation is adequate for the existing pump the problem occurs due to the Gas Phase. There is a static head available created by the difference of the Vessel level to the pump inlet plus the pump’s can length but this Head cannot remove from the already dissolved Vapor Gas Phase. In order this pump to be able to operate satisfactory the dissolved Gas should be less than 10%, from the information sent we suspect that this percentage is much higher and consequently the result is to have symptoms similar to cavitation. When originally quoted this pump the information given was that Temperature would be 50deg.C (normal) and pressure 147 mbar, in this condition the fluid in the Vessel would be still in water phase (below boiling point) and there would not be a problem for the pump to operate. There was a mention for 100 deg.C as max temperature but this was mentioned as some extreme case and there was no mention for the pressure at this temperature (we considered that customer would assure adequate pressure in order to avoid boiling conditions). So our suggestion would be to change the pump type from Centrifugal Can type to a Side Channel pump, the reason is because the side channel pump has the ability to operate well with ~50% dissolved gas phase. From the information we get from below drawing (and photo) if install a side channel pump with its suction nozzle at the level of the existing pump the NPSHa will be ~1.5m (at least) UNQUOTE
Part 1 – GENERAL
1.1 THE REQUIREMENT
| 1. Supply new VS6 vertical pump with suitable coupling (with/without Motor) as attached Specification, most of critical points: |  |  |  | m3/hr /m | l/s /m | m3/s m
|  | · Suction Specific Speeds at BEP shall not exceed 12,800 (m3/h, r/min, meters), 11,000 (GPM,r/min, feet) |  | gpm/feet | 1.1637 | 9.7243 | 0.019403
|  | · The pump bowl efficiency not less than 67%, |  |  | gpm/feet
|  | · NPSHA shall exceed NPSHR3 by at least 1 m throughout the entire operating range, from minimum continuous stable flow up to and including rated capacity and by a minimum of 0.3m at maximum system capacity at End Of Curve (EOC), |  | m3/s m | 51.6552
|  | · MCSF shall not less than 50% of BEP flow. |  | m3/hr /m | 0.86083 | 11018.6809
|  | · The pump horsepower demand did not exceed the rated motor hp beyond the 1.0 service rating at any point of operation points. |  | l/s /m | 1.6195
· The minimum efficiency index (MEI) ≥ 0.70
2. Study the intended application and operation of the pump system, to replace the VS6 pump with other possible options such as employing booster plus main pump etc. and recommend the possible option which best satisfy the indicated requirements techno-economically
1.2 DOCUMENT SUBMITTALS
· Provide detailed design review submittal (shop drawings) regarding the proposed equipment, materials, components, hardware, construction, performance, operation, assembly, weight, dimensions and other technical information for review to confirm conformance to the criteria provided herein and as otherwise may be applicable.
· Provide performance curves showing head, flowrate, NPSHr, efficiency, submergence, etc.
· Provide signed and dated certified factory test data reports for pressure and performance tests as given below for review prior to shipping.
· Provide detailed operation and maintenance manuals for review for the equipment with equipment summary, operational procedures, preventative maintenance procedures, parts list, approved shop drawings, safety procedures, and documentation of warranties, affidavits and certifications that may be required.
· Certify in writing proper installation, commissioning and field testing.
· Provide 18-month 100% manufacturer’s warranty from date of shipping for defective materials and workmanship.
· Provide manufacturer recommended spare parts list for review.
1.3 QUALITY ASSURANCE
1. Pumps Performance and NPSH tests – WITNESSED by SEPCO Engineers
· Pump shall be factory tested (measurement of capacity, head, absorbed power, pump’s efficiency) according to ISO 9906 procedures or equivalent standard e.g., API 610 11th Edition, or ANSI/HI 14.6, tolerance of the measurements shall be according to ISO 9906, grade 2B, or equivalent standard e.g., API 610 11th Edition, or ANSI/HI 14.6 for the guaranteed point.
· Tests shall be performed using the complete and assembled pump bowl system.
· A minimum of five hydraulic test readings between shutoff head and 25 percent beyond the maximum indicated capacity.
· Stuffing box pressure shall be recorded during performance and NPSH tests and shall be tested at minimum submergence of the pump
· Due to the system configuration have a minimum flow protection using recycle line with restriction orifice 11.3 mm; Vendor/Supplier shall provide a means to determine the onset of recirculation at or near the minimum continuous stable flow during the performance test.
· Frequency analysis of shaft vibration (in order to detect cavitation) shall be performed during the performance test. During the pump performance test, there shall be no sign of cavitation (either vibration or noise) in the full operating range of the pump from minimum continuous stable flow up to maximum flow rate within the 'allowable operating region of flow'
· Shop tests shall be carried out with an electric motor with known efficiency values
· The costs of flight tickets and a full accommodation (Hotels, Meals and local transportations) for two of SEPCO’s engineers to witness the test shall be borne by the Vendor/Supplier
2. Hydrostatic Test - Non-Witnessed
At 1,5 times the pipe system design pressure, during 30 minutes for all equipment under pressure is included.
3. Material Certificates acc. EN 10204 type 3.1
shall be provided for pump main parts (Rotating components (shaft, impeller, sleeves etc.), Shaft seals, Diffusers and other static metallic parts inside the pump),
The charges for third party inspection will be borne by the Vendor/Supplier.
4. In case pump will supplied without motor Certification that the pump horsepower demand did not exceed the rated motor hp beyond the 1.0 service rating at any point on the operational curve. Existing motor size is listed in excel file sheets named Motor Name Plate and Motor Flange
PART 2 – EXECUTION
2.1 PUMP INSTALLATION AND COMMISSIONING
A- Pump equipment will be field assembled and installed as part of this work, and these costs shall be included in the Vendor/Supplier scope or pricing.
B- The factory authorized service representative of the pump manufacturer shall be present at the site for three working days to furnish the commissioning services as follows to assure and certify proper installation, alignment, correct fit of driver fixing bolts with driver foot, measured and contract coupling fitted, lubrication, and adjustment of the equipment and readied for operation. Observe and otherwise provide the following services.
1. Installation of the equipment.
2. Inspection, checking, and adjusting the equipment.
3. Start-up and field testing for proper operation, and protection system.
4. Field adjustments to ensure that the equipment installation and operation comply with the manufacturer’s requirements.
C- The following field testing shall be conducted:
1. Startup, check, and operate the pump system over its entire speed range. Vibration shall be tested and proved within the amplitude limits recommended by the Hydraulic Institute Standards at a minimum of four pumping conditions representative of the planned operation points for the respective pump.
2. Pump performance evaluation: The analysis of the guarantee point(s) shall be done through the capture of three (3) test points (one at the rated flow, one at the normal flow and one at the MCF. Where no permanent flow instruments available at site, Vendor/Supplier shall make necessary arrangements (such as clamp type ultrasonic flow meters to avoid modifications at site).
3. Vibration acceptance test: Frequency analysis of shaft vibration (in order to detect cavitation) shall be performed during the performance test. During the pump performance test, there shall be no sign of cavitation (either vibration or noise) in the full operating range of the pump from minimum continuous stable flow up to maximum flow rate within the “allowable operating region of flow”
· The following tables summarize the mechanical acceptance criteria for the centrifugal pump, and the electrical motor
|  | Centrifugal pump Radial Vibrations (μm pk to pk unfiltered) : | As per ISO 10816-3 Zone boundary A/B OR 50 OR 66% of alarm values whichever is less
|  | Electric motor Radial vibrations (μm pk to pk unfiltered): | 50 OR 66% of alarm limit chosen based on ISO 7913 / ISO 10816
· Any stable discrete, non-synchronous vibration exceeding 20% of the allowable vibration as defined in Table above shall be cause of rejection. Any unstable non synchronous vibration shall be cause of rejection.
4.Obtain concurrent readings of motor voltage, amperage, water level, flowrate, and pump discharge head conditions at each pump rotational speed. Check each power lead to the existing motor for proper current balance.
2.2 TRAINING
The training representative of the pump manufacturer shall be present at the site for three working days to provide the following training services.
1. Instruct the Owner’s personnel in the operation and maintenance of the equipment, including step-by-step troubleshooting with necessary test equipment. Instruction shall be specific to the equipment provided.
2. The representative shall have at least five years’ experience in training. A resume for the representative shall be submitted.
3. Training shall be scheduled a minimum of three weeks in advance of the first session.
4. Proposed training material and a detailed outline of each lesson shall be submitted for review. Comments shall be incorporated into the material. The training materials shall remain with the trainees.
5. The Owner may videotape the training for later use with the Owner personnel

## System Desc.
System descrbtion
Tank Details and sytem photos | PID and ISO DWG in attched File
Clean Drain Flash Tank:
The clean drain flash tank (30LCM50 BB001) receives the fluid drained by
gravity or pressure during start-up through four 6” LP, CRH, HRH and HP drain
headers (manifolds). The manifolds separate HP, IP and LP steam and water
drains. The clean drain water is pumped out of the clean drain flash tank by
vertical 1x100% clean drain pump (30LCM70 AP001) to quenched blowdown
water collection pit.
* High liquid level in the clean drain flash tank sensed by the level transmitter
(30LCM50 CL001) starts the clean drain pump (30LCM70 AP001)
* Low Low liquid level sensed by the level transmitter (30LCM50 CL001) shall stop
the clean drain pump (30LCM70 AP001), thereby protecting the pumps from cavitation.
* Clean drain pump (30LCM70 AP001) is provided with a minimum flow protection
using recycle lines with restriction orifice (30LCM60 BP001).
Tank Details
distance from Tank outlet flange to pump suction flange 1600 mm

## Pump Spec
VERTICAL WET SUCTION CAN TYPE PUMP, with suitable coupling, With/Without Motor
1 | GENERAL
| ITEM (KKS) | 30LCM /70 AP001
| Service | Clean Drain Pump
| Quantity | 1 * 100%
| Type | VS6 (suction and discharge are at same elevation) Vertical wet suction can type
| ATEX Category (NOTE 4) | NOT QUALIFIED
2 | DESIGN CONDITIONS
| Fluid Type |  | Condensate water
| System design gauge pressure | (bar,g) | Inlet= 2, full vacuum Outlet= 28, full vac.
| System design temperature | (°C) | Inlet= 110 Outlet=110
| Fluid Viscosity | (kg/m.s) | 546.833E-06 @50 deg. C
| Fluid Density | (kg/m3) | 958 @ 1000C
| Fluid Vapor absolute pressure | (bar,a) | 0.147
| Fluid PH |  | 8-10
| Water chemistry of Combined Cycle Power Plants |  | amonia is used to control PH range (9-10) and sometime an oxygen scavenger (carbohydrazined) used if feedwater oxygen concentration is above 10 ppb
| Barometric absolute pressure | (mbar,a) | 946
| Ambient temperature | (°C) (max / min) | 43 / -0.8
| Relative humidity | (%) | 3.5% - 98%
| Location | (Outdoor/ Indoor) | Indoor (ST building)
3 | Operating conditions SPECIFICATION
| Operating conditions |  | Shut Off | Minimum flow | Design Point | Runout flow
| Flow | (m3/h) | 0 | 6 | 20 | 40
| Total Head | (m) | 43 | 39.2 | 32.66 | 15.5
| Discharge pressure | (bara)
| Temperature | (°C) | 100 | 100 | 100 | 100
| Nominal suction pressure -condenser pressure | (bara) | N/A | N/A | N/A | N/A
| NPSHa (suction nozzle level), | (m) |  | 0.47 | 0.47 | 0.47
| Pump efficiency | (%) |  | 36 | 67 | 57
| NPSH required (NOTE 1) | (m) | N/A | 1.1 | 1.1 | 1.5
| Brake horsepower | (kW) |  | 1.78 | 2.55 | 2.84
| Total head at shutoff condition | (m) | 43
| Maximum gauge pressure at shutoff condition | (bar) | 4.04
| NPSH available (NOTE 1) | (m) | 2.77
| NPSH available (NOTE 5) | (m) | 0.47
| Speed | r.p.m. | 1500
| First critical speed | (r.p.m.) | >2100
| Specificic speed of the first impeller | (USA units) | 2889
| Suction specificic speed of the first impeller | (USA units) | 6365
| Design pressure of can | (barg) | 6
| Design pressure of bowl, colum and discharge head | (barg) | 10
| Design temperature of pump | (°C) | 110
| Maximum operation time at shut-off condition | (s) | not recommended
| Pump rotation ( NOTE 3) | CW or CCW | CCW
| Noise level 1 m away from the pump-motor assembly | (dBa) | <85
4 | CONSTRUCTION FEATURES
| Number of stages | 3
| Suction Nozzle (DN400) | Position | Size | Flange class | Flange Rating | Faces
|  | Above soleplate | DN 400 | ANSI | # 150 | RF
| Discharge Nozzle (DN 300) | Position | Size | Flange class | Flange Rating | Faces
|  | Above soleplate | DN 300 | ANSI | # 150 | RF
| First pump stage | Single suction
| Impellers | First Impeller | Enclosed
Dmax=133 Dactual=133 Dmin=105
|  | Second and other impellers | Enclosed
Dmax=133 Dactual=120 Dmin=105
| Shaft sealing | Mechanical seal |  Pumped fluid (When pump in operation) |  | Make: To be Specified
|  |  |  Flushing from the operating pump (When pump is not operating) |  | Flushing N° : Q= l/min PS = μm p= barg. T= °C
| Bearings | Line shaft | Pumped fluid |  | Q= l/min PS = μm p= barg. T= °C
|  | Thrust | Oil |  | Q= l/min PS = μm p= barg. T= °C
| Auxiliary connections | Denomination | Type |  | Notes
|  | Drain of can | Connection |  | Outlet pipe with flanged end
External
|  | Vent of can | Connection |  | Flanged end
|  | Vent connection | Connection |  | Pump discharge
|  | Manometer | Connection |  | Pump suction and pump discharge
| Anchor bolts | Supply | Information
| Coupling | Flexible , NO Spacer | provide suitable Coupling
| Baseplate | Driver pedestal/Head
5 | Existing MOTOR SPECIFICATION
| Manufacturer |  | WEG W22 Frame:112 M/ Mounting: P5
| Power (NOTE 6) |  | 4 Kw
| Speed (r.p.m.) |  | 1440
| Minimum driver efficiency (%) at design point |  | 86.7
| Cooling fluid / Type |  | Air / IC411
6 | PUMP MATERIALS (Specified)
| Inlet bell |  | Cast Steel ASTM A-216 WCB
| Can |  | Welded Steel DIN St 37.2
| Casings |  | Cast Steel ASTM A-216 WCB
| Impellers |  | Stainless Steel ASTM A-743 Gr. CF8M
| Diffusers |  | Cast Steel ASTM A-216 WCB
| Shaft |  | Stainless Steel A276 - 420, Surface Hardness RC-30
| Column pipe |  | Welded Steel DIN St 37.2
| Discharge elbow/ head |  | Welded Steel DIN St 37.2
| Casing wear rings |  | ASTM A-743 Gr. CF8M
| Impeller wear rings |  | ASTM A-743 Gr. CF8M
7 | MECHANICAL DATA
| Moment of inertia WD2 | (N. m2) | TBD
| Nominal pump torque | (N. m) | TBD
| Maximum required torque during starting | (N. m) | TBD
| Maximum required torque at run-out conditions | (N. m) | TBD
| Maximum torque which pump is able to withstand | (N. m) | TBD
| Maximum applicable transient taking into account safety | (N. m) | TBD
| Maximum forces and moments at pump inlet nozzle (as per API 610 values) |  | Forces (N) Fx= Fy= Fz=
Moments (N. m) Mx= My= Mz=
| Maximum forces and moments at pump discharge nozzle (as per API 610 values) |  | Forces (N) Fx= Fy= Fz=
Moments (N. m) Mx= My= Mz=
| Weights |  | Pump (kg)= Motor (kg)=
Driver pedestal/ Head (kg)= Total (kg)=
| Thrust Load-- Downward | Maximum (N) | TBD
|  | Continous (N) | TBD
8 | REMARKS
(1) Referred to the first impeller eye . The pumps NPSH will be designed with a safety margin of 1 m above maximum required NPSH, whichever is larger.
(3) Viewed from the drive to the pump
(4) The pumps will not be ATEX qualified
(5) Referred to suction nozzle
(6) The pump and driver are able to operate through run out flow.

## PUMP SECTIONAL DRAWINGS
PUMP SECTIONAL DRAWINGS WITH MATERIAL LISTS

## Motor Name Plate
Motor Available on site

## Motor Flange
Motor Flange Dim