## pricing schedule
Serial No | DWG | Item Desc. |  | Item # based on DWG | Dimension | Notes and Spec. |  | Qty | Unit Price | Total Price
1 | GT Inlet Expansion Joint Bachman FJ1250GT Dwg.#208201 (⌀5459 ID X 575 GTJ-HC.) | Inlet EJ Belt |  | Item#14 |  | punched 120 holes in each side as below Drawing, |  | 2 set
1 set made up of 3 Pieces each one (1.688” thick x 15½” W x 296” LG)
open ended, with PFA heat sealing film (splice film for field splicing),
Spec according to point 8+9 in General Requirements
1.1 |  | installation hardware for Serial #1 (just for 1 set) | Item Description | Item # | Designation | Type | Material List Description | Qty
|  |  | INLET BELT STUD fully threaded | 4.1 | M12 (51mm [2”] LONG) | 304 SS |  | 120
|  |  | OUTLET BELT SIUO fully threaded | 4.2 | M12 (51mm [2”] LONG) | A36 |  | 120
|  |  | INLET BELT HEX NUT | 5.1 | M12 | 304 SS |  | 120
|  |  | outlet belt hex nut | 5.2 | M12 | A36 |  | 120
|  |  | Flat Washer | 6 |  | A36 |  | 240
|  |  | NSULATON RETAINER CLIP Rock wool Perforated Insulation Pins for Insulating Nails, Self-Locking Washers, Flat Washer Round. | 12 | 10GA X 36 mm [1½”] OD Clips | 304 SS |  | 240
2 |  | Dome Seal Pillow |  | Item#15 | 1 set made up of 3 Pieces each one (1” thick x 30¾” W x 294” LG) | 1” CERAMIC BLANKET, SILICA CLOTH WRAP, and 0.011” S.S WIRE KNIT TUBE WRAP |  | 2 set
Spec according to point 10 in General Requirements
3 |  | Cavity Filler Pillow |  | Item#16 | 1 set made up of 3 Pieces each one (6” thick x 3” W x 294” LG) | 1” CERAMIC BLANKET, 0.07” FIBERGLASS CLOTH |  | 1 set
Spec according to point 10 in General Requirements
4 | Bypass Expansion Joint Bachman FJ1250GT Dwg.# 224107 (6000 x 6000 x 411 GTJ-CC) | Inlet EJ Belt |  | Item#15 | 1 set made up of 3 Pieces each one (1” thick x 24⅝” W x 387” LG) | punched 120 holes in each side as below Drawing, |  | 1 set
open ended, with PFA heat sealing film (splice film for field splicing),
Spec according to point 8+9 in General Requirements
5 |  | Dome Seal |  | Item#16 | 1 set made up of 3 Pieces each one (1” thick x 24⅝” W x 339” LG) | 1” CERAMIC BLANKET, SILICA CLOTH WRAP, and 0.011” S.S WIRE KNIT TUBE WRAP |  | 1 set
Spec according to point 10 in General Requirements

## Compliance Sheet
S/N | REQUESTED |  | Yes/NO | PROVIDED BY VENDOR
Design Data
1 | Design Data for items (1-3)
2 | Design Data for items 4-5
3 | Diverter Damper System Design
General Requirements:
1 | All expansion joints shall be shipped fully assembled, where size permits, and ready for bolting and seal welding to the mating flanges.
2 | Expansion joints shall be precompressed as required to allow for gasket installation.
3 | Expansion joints shall be designed and fabricated to align with the gas turbine and HRSG inlet flange connections and stack and bypass flange connections. As attached drawing
4 | The design, material, construction, manufacture, inspection, and testing of the expansion joints must comply with the requirements of the Expansion Joint Manufacturer Association (EJMA) standards in the USA and the Fluid Sealing Association, USA.
5 | Nonmetallic expansion joints of gastight construction and low noise design shall be provided
6 | Expansion joints shall be designed to withstand full system operating temperatures and pressures, including unexpected pressure variations or excursions.
7 | Internal design pressures shall be the same as for the ductwork.
8 | Composite Belt Construction:
8.1 | The composite belt shall be made up of several layers.
8.2 | The flat belt system shall consist of an outer gas seal reinforced base ply, multiple insulating plies, and wire reinforced inner layer.
8.3 | The insulating plies shall be of sufficient layers or thickness to provide thermal protection for the outer ply, preventing it from being exposed to the process gas..
8.4 | The insulating plies must be flexible to accommodate duct movement without losing their insulating properties.
8.5 | The flat belt shall be completely sealed with no exposed edges of stitching. The belt shall be fitted with an insulating cuff wrapped around the edge between the hot frame and the belt, and the backup bar and the belt.
8.6 | The belt shall not be directly exposed to the hot frame.
8.7 | The belt shall be suitable for (691º C) temperature service at ±3 psi (20 kPa) pressure across the belt.
8.8 | The cover ply material shall be fiberglass reinforced, virgin (0.090 inch [2.3 mm]) fluoroelastomer manufactured by one of the manufacturers listed in table below,
| Component | Manufacturer
| Fiberglass expansion joint cover ply material | Dupont - Viton B; 3M - Flourel; Chemical Fabrics Corp. Darlyn - 1100CB; Dynex FP500L; Damper Design; Dynex - RM; Expansion Joint Systems; Insulcon; KE - Burgmann; LBH; Microflex; Townson; Boarding; Kempchen IPAR; or SPERI
9 | Insulation Plies:
9.1 | The insulation plies shall be of ceramic fiber.
9.2 | The inner ply shall be aluminized fiberglass fabric.
9.3 | The inner ply shall have a retaining wire mesh of Type 309 stainless steel.
10 | Insulation Pillows:
10.1 | The insulation pillow shall be designed to completely fill the volume between the inlet and outlet frame and the liner, protecting the composite belt from exhaust gas.
10.2 | They should be capable of both axial compression and lateral expansion.
10.3 | The pillows should have a stainless steel mesh outer covering.
10.4 | They need to be capable of continuous operation at a high temperature of (976º C).
10.5 | The outer protective covering of the insulation pillows should be Type 309 stainless steel mesh.
10.6 | The insulation pillow shall be of silica fabric reinforced with Inconel wire capable of continuous (976º C) operation.
10.7 | The inner pillow insulation fill shall be high strength (100 kg/m 3) ceramic blanket rated for (691º C).